# Infection Control Risk Assessment (ICRA):

# Matrix of Precautions for Construction and Renovation

# Step 1. Using the following table, identify the Type of construction project activity (Type A–D).

| #### TYPE A | Inspection and noninvasive activities Includes, but is not limited to, the following: - Removal of ceiling tiles for visual inspection only (for example, limited to one tile per 50 square feet) - Painting (but not sanding) - Wall covering, electrical trim work, minor plumbing, and activities that do not generate dust or require cutting of walls or accessing ceilings other than for visual inspection |
| --- | --- |
| #### TYPE B | Small-scale, short-duration activities that create minimal dust Includes, but is not limited to, the following: - Installation of telephone and computer cabling - Access to chase spaces - Cutting of walls or ceilings where dust migration can be controlled |
| #### TYPE C | Work that generates a moderate to high level of dust or requires demolition or removal of any fixed building components or assemblies Includes, but is not limited to, the following: - Sanding of walls for painting or wall covering - Removal of floor coverings, ceiling tiles and casework - New wall construction - Minor duct work or electrical work above ceilings - Major cabling activities - Any activity that cannot be completed within a single work shift |
| #### TYPE D | Major demolition and construction projects Includes, but is not limited to, the following: - Activities that require consecutive work shifts - Activities that require heavy demolition or removal of a complete cabling system - New construction |

Step 1_______________________________________________________________________

Step 2. Using the following table, identify the Patient Risk Groups that will be affected.

If more than one risk group will be affected, select the higher risk group.

| Low Risk | Medium Risk | High Risk | Highest Risk |
| --- | --- | --- | --- |
| - Office areas | - Cardiology - Echocardiography - Endoscopy - Nuclear medicine - Physical therapy - Radiology/MRI - Respiratory therapy | - Critical care unit - Emergency room - Labor and delivery - Laboratories (specimen) - Medical units - Newborn nursery - Outpatient surgery - Pediatrics - Pharmacy - Postanesthesia care unit (PACU) - Surgical units | - Any area caring for immunocompromised patients - Burn unit - Cardiac cath lab - Central sterile supply - Intensive care unit - Negative pressure isolation rooms - Oncology - Operating rooms, including C-section rooms |

Step 2_____________________________________________________________

Step 3. Match the . . .

Patient Risk Group (Low, Medium, High, Highest) with the planned …

Construction Project Type (A, B, C, D) on the following matrix, to find the …

Class of Precautions (I, II, III or IV) or level of infection control activities required.

Class I–IV Precautions are delineated on the following page.

### IC Matrix—Class of Precautions: Construction Project by Patient Risk

Construction Project Type

| Patient Risk Group | TYPE A | TYPE B | TYPE C | TYPE D |
| --- | --- | --- | --- | --- |
| LOW Risk Group | I | II | II | III/IV |
| MEDIUM Risk Group | I | II | III | IV |
| HIGH Risk Group | I | II | III/IV | IV |
| HIGHEST Risk Group | II | III/IV | III/IV | IV |

Note: Infection Prevention and Control approval will be required when the Construction Project Type and Patient Risk Group indicate that Class III or Class IV control procedures are necessary.

Step 3_____________________________________________________________

Description of Required Infection Control Precautions by Class

During Construction Project				Upon Completion of Project

| CLASS I | - Execute work using methods to minimize raising dust from construction operations. - Immediately replace a ceiling tile displaced for visual inspection. | 1. Clean work area upon completion of the task. |
| --- | --- | --- |
| CLASS II | - Provide active means to prevent airborne dust from dispersing into the atmosphere. - Water mist work surfaces to control dust while cutting. - Seal unused doors with duct tape. - Block off and seal air vents. - Place dust mat at entrance and exit of work area. - Remove or isolate the heating, ventilation, and air conditioning (HVAC) system in areas where work is being performed. | - Wipe work surfaces with cleaner/disinfectant. - Contain construction waste before transport in tightly covered containers. - Wet mop and/or vacuum with high-efficiency particulate air (HEPA) filtered vacuum before leaving work area. - Upon completion, restore HVAC system where work was performed. |
| CLASS III | - Remove or isolate HVAC system in areas where work is being done to prevent contamination of duct system. - Complete all critical barriers (that is, sheetrock, plywood, plastic) to seal work area from nonwork area or implement control cube method (cart with plastic covering and sealed connection to work site with HEPA vacuum for vacuuming prior to exit) before construction begins. - Maintain negative air pressure within work site, utilizing HEPA-equipped air filtration units. - Contain construction waste before transport in tightly covered containers. - Cover transport receptacles or carts. Tape covering unless lid is solid. | - Do not remove barriers from work area until completed project is inspected by the owner’s safety department and infection prevention and control department and thoroughly cleaned by the owner’s environmental services department. - Remove barrier materials carefully to minimize spreading of dirt and debris associated with construction. - Vacuum work area with HEPA-filtered vacuums. - Wet mop area with cleaner/disinfectant. - Upon completion, restore HVAC system where work was performed. |
| CLASS IV | - Isolate HVAC system in area where work is being done to prevent contamination of duct system. - Complete all critical barriers (that is, sheetrock, plywood, plastic) to seal work area from nonwork area or implement control cube method (cart with plastic covering and sealed connection to work site with HEPA vacuum for vacuuming prior to exit) before construction begins. - Maintain negative air pressure within work site utilizing HEPA-equipped air filtration units. - Seal holes, pipes, conduits, and punctures appropriately. - Construct anteroom and require all personnel to pass through this room so they can be vacuumed using a HEPA vacuum cleaner before leaving work site or they can wear cloth or paper coveralls that are removed each time they leave the work site. - All personnel entering work site are required to wear shoe covers. Shoe covers must be changed each time the worker exits the work area. | - Do not remove barriers from work area until completed project is inspected by the owner’s safety department and infection prevention and control department and thoroughly cleaned by the owner’s environmental services department. - Remove barrier material carefully to minimize spreading of dirt and debris associated with construction. - Contain construction waste before transport in tightly covered containers. - Cover transport receptacles or carts. Tape covering unless lid is solid. - Vacuum work area with HEPA-filtered vacuums. - Wet mop area with cleaner/disinfectant. - Upon completion, restore HVAC system where work was performed. |

Step 4. Identify the areas surrounding the project area, assessing potential impact.

| Unit Below | Unit Above | Lateral | Lateral | Behind | Front |
| --- | --- | --- | --- | --- | --- |
| Risk Group | Risk Group | Risk Group | Risk Group | Risk Group | Risk Group |

Step 5. Identify specific site of activity, for example, patient rooms, medication room, and so on.

__________________________________________________________________

Step 6. Identify issues related to: ventilation, plumbing, and electrical in terms of the occurrence of probable outages.

__________________________________________________________________

Step 7. Identify containment measures, using prior assessment. What types of barriers (for example, solids walls)? Will HEPA filtration be required?

_________________________________________________________________

Note: Renovation/construction area shall be isolated from the occupied areas during construction and shall be negative with respect to surrounding areas.

Step 8. Consider potential risk of water damage. Is there a risk due to compromising structural integrity (for example, wall, ceiling, roof)?

Step 9. Work hours: Can or will the work be done during non-patient-care hours?

Step 10. Do plans allow for adequate number of isolation/negative airflow rooms?

Step 11. Do the plans allow for the required number and type of hand-washing sinks?

Step 12. Does the infection prevention and control staff agree with the minimum number of sinks for this project? (Verify against Facility Guidelines Institute (FGI) design and construction guidelines for types and area.)

Step 13. Does the infection prevention and control staff agree with the plans relative to clean and soiled utility rooms?

Step 14. Plan to discuss the following containment issues with the project team, for example, traffic flow, housekeeping, debris removal (how and when).

_________________________________________________________________

_________________________________________________________________

_________________________________________________________________

Identify and communicate the responsibility for project monitoring that includes infection prevention and control concerns and risks. The ICRA may be modified throughout the project. Revisions must be communicated to the project manager.

Note: This form is often referred to as the ASHE [American Society for Healthcare Engineering] ICRA document. It is an example of a form that organizations can adapt for use in their own facilities. While it is a useful tool, organizations should use the form as a source for creating their own matrix that specifically addresses the scope, needs, and characteristics of the particular organization. Simply using the tool “as is” may not provide the most targeted assessment. In addition, organizations should be aware that this particular form does not include assessments of utilities, noise, vibration, airflow, and emergency procedures. These are items that The Joint Commission requires as part of the preconstruction risk assessment.

Sources: Steps 1–3 adapted with permission from V. Kennedy, B. Barnard, St. Luke Episcopal Hospital, Houston; C, Fine, CA. Steps 4–14 adapted with permission from Fairview University Medical Center, Minneapolis. Forms modified/updated and provided courtesy of Judene Bartley, ECSI, Inc., Beverly Hills, MI, 2002. Updated November 2008.